## Sheet1
Transmission System Availability for Interconnecting Transformers in Uttarakhand For The Month Of : Febuary 2019 | [19 empty] | Form 2-2
No. | Name of Division | Name of the Transmission Element | [A] Time Considered for Availability after excluding outage hours not attributable to Transmission Licensee |  | [B] Time of shutdowns/manual trippings not attributable to transmission licensee and deemed to be available |  |  |  |  | [C] Time of breakdowns/automatic trippings/shutdowns attributable to Transmission licensee not included in [B] |  |  | Total time in the period, H = 24x60x(No. of days in the period)=1440xD | Total time considered during the period under consideration | Non availability time considered | Time of availability considered | MVA capacity for ICT | No. for ICT | Weightage factor (W) | Weightage factor*No. of hrs of availability/Total hrs considered during the period under consideration
|  |  | Outage of elements due to acts of God and force Majeure beyond the control of Transmission Licensee. | Outage caused by grid incident/disturbance not attributable to Transmission Licensee. | Shutdown of Transmission licensee's element due to distribution licensee/other agencies requirement of carrying out maintenance or construction of their system. | Shutdown of Transmission licensee's element due to distribution licensee for scheduled load shedding. | Shutdown of Transmission licensee's element due to distribution licensee for un-scheduled load shedding. | Outage due to manual tripping of transmission licensee's line due to over voltage. | Shutdown of Transmission licensee's element on account of manual tripping of switced bus reactor as per directions of SLDC/RLDC. | Non availability time causing loss of generation . | Non availaibility time causing only load shedding/power cut for distribution licensee. | Non availability time neither causing generation loss nor causing load shedding/power cut for distribution licensee.
|  |  | (Minutes) | (Minutes) | (Minutes) | (Minutes) | (Minutes) | (Minutes) | (Minutes) | (Minutes) | (Minutes) | (Minutes) | (Minutes) | (Minutes) | (Minutes) | (Minutes)
(i) |  | (ii) | (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k) | (T)=(k)-(a)-(b) | (TN)=2(h)+2(i)+(j) | (l)=(T)-(TN) | (m) | (n) | (W)=(m)x(n) | (AV)=(W)x(l)/(T)y
Interconnecting Transformers(ICT)
I | 315 MVA
1 | E (O&M) 400 KV Kashipur | 315 MVA T/F-I at KSP-4 S/S | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 315 | 1 | 315 | 315 | 1
2 |  | 315 MVA T/F-II at KSP-4 S/S | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 315 | 1 | 315 | 315 | 1
II | 240 MVA
3 | E (O&M) 400 KV Rishikesh | 240 MVA T/F (BHEL) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 240 | 1 | 240 | 240 | 1
4 |  | 315 MVA T/F at (RKSH-220) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 315 | 1 | 315 | 315 | 1
III | 160 MVA
5 | E (O&M) 400 KV Kashipur | 160 MVA T/F-I at KSP-4 S/S | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 160 | 1 | 160 | 160 | 1
6 |  | 160 MVA T/F-II at KSP-4 S/S | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 160 | 1 | 160 | 160 | 1
7 | E (O&M) 220 KV Pantnagar | 160 MVA T/F-I at Pant Nagar-220 KV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40320 | 40320 | 5 | 40315 | 160 | 1 | 160 | 159.9802 | 0.99988
8 |  | 160 MVA T/F-II at Pant Nagar-220 KV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40320 | 40320 | 5 | 40315 | 160 | 1 | 160 | 159.9802 | 0.99988
9 | E (O&M) 220 KV Rishikesh | 160 MVA T/F-I (BHEL) (RKSH-220) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 160 | 1 | 160 | 160 | 1
10 |  | 160 MVA T/F-II (CGL) (RKSH-220) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 160 | 1 | 160 | 160 | 1
11 |  | 160 MVA T/F-III (IMP) (RKSH-220) New | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 160 | 1 | 160 | 160
12 | E (O&M) 220 KV Roorkee | 160 MVA T/F-I(RKE-220) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 160 | 1 | 160 | 160 | 1
13 |  | 160 MVA T/F-II(RKE-220) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 160 | 1 | 160 | 160 | 1
14 | E (O&M) 220 KV Jhajhra | 160 MVA 220/132 KV T/F-Ist at Jhajhra | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 160 | 1 | 160 | 160 | 1
15 |  | 160 MVA 220/132 KV T/F-IIst at Jhajhra | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 160 | 1 | 160 | 160 | 1
16 | E (O&M) SIDCUL HRD | 160 MVA T/F-Ist (SIDCUL) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 40320 | 40320 | 34 | 40286 | 160 | 1 | 160 | 159.8651 | 0.99916
17 |  | 160 MVA T/F-IInd (SIDCUL) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 40320 | 40320 | 34 | 40286 | 160 | 1 | 160 | 159.8651 | 0.99916
IV | 100 MVA
18 | E (O&M) 220 KV Haldwani | 100 MVA T/F-I 220/132 KV (HLD-220) | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40300 | 0 | 40300 | 100 | 1 | 100 | 100 | 1
19 |  | 100 MVA T/F-II 220/132 KV (HLD-220) | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40300 | 0 | 40300 | 100 | 1 | 100 | 100 | 1
20 | E (O&M) 220 KV Mahuakherganj | 100 MVA T/F-I at 220 KV S/S MKG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 100 | 1 | 100 | 100 | 1
21 |  | 100 MVA T/F-II at 220 KV S/S MKG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 100 | 1 | 100 | 100 | 1
22 | E (O&M) 220 KV Roorkee | 100 MVA T/F-I 220/132 KV (Pirankaliyar) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 100 | 1 | 100 | 100
23 |  | 100 MVA T/F-I 220/132 KV (Pirankaliyar) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 100 | 1 | 100 | 100
V | 80 MVA
24 | E (O&M) Jhajhra S/S | 80 MVA T/F-II at Jhajhra S/S | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 80 | 1 | 80 | 80 | 1
25 | E (O&M) SIDCUL HRD | 80 MVA T/F-Ist (SIDCUL-220) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 708 | 0 | 40320 | 40320 | 1416 | 38904 | 80 | 1 | 80 | 77.1905 | 0.96488
26 |  | 80 MVA T/F-II (SIDCUL-220) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571 | 0 | 40320 | 40320 | 1142 | 39178 | 80 | 1 | 80 | 77.7341 | 0.97168
27 | E (O&M) 220 KV Pantnagar | 80 MVA T/F-I at Pant Nagar-220 KV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 80 | 1 | 80 | 80 | 1
28 |  | 80 MVA T/F-II at Pant Nagar-220 KV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 80 | 1 | 80 | 80 | 1
29 | E (O&M) 132 KV Kashipur | 80 MVA T/F at 132 KV S/S BAZPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 80 | 1 | 80 | 80 | 1
30 | E (O&M) 220 KV Mahuakherganj | 80 MVA T/F-I at 220 KV S/S MKG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 80 | 1 | 80 | 80 | 1
31 |  | 80 MVA T/F-II at 220 KV S/S MKG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 40320 | 40320 | 26 | 40294 | 80 | 1 | 80 | 79.9484 | 0.99936
VI | 50 MVA
32 | 50MVA T/F Roorkee | 50 MVA T/F-I 220/33 KV (Pirankaliyar) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 50 | 1 | 50 | 50 | 1
33 |  | 50 MVA T/F-II 220/33 KV (Pirankaliyar) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26565 | 40320 | 40320 | 26565 | 13755 | 50 | 1 | 50 | 17.0573 | 0.34115
34 |  | 50 MVA T/F-I ROORKEE220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 40320 | 40320 | 87 | 40233 | 50 | 1 | 50 | 49.8921 | 0.99784
35 |  | 50 MVA T/F -II ROORKEE220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 50 | 1 | 50 | 50 | 1
36 | E (O&M) SIDCUL HRD | 50 MVA T/F (SIDCUL-220) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 40320 | 40320 | 286 | 40034 | 50 | 1 | 50 | 49.6453 | 0.99291
37 | E (O&M) 220 KV Srinagar | 50 MVA 220/33kV T/F (CHAMBA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 40320 | 40320 | 25 | 40295 | 50 | 1 | 50 | 49.969 | 0.99938
38 | E (O&M) 220 KV Pantnagar | 50 MVA T/F-I Pant Nagar 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 40320 | 40320 | 732 | 39588 | 50 | 1 | 50 | 49.0923 | 0.98185
39 |  | 50 MVA T/F-II Pant Nagar 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 40320 | 40320 | 732 | 39588 | 50 | 1 | 50 | 49.0923 | 0.98185
40 | E (O&M) Dehradun | 50 MVA 220/33 KV T/F-Ist at IIP Harrawala | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 40320 | 40298 | 119 | 40179 | 50 | 1 | 50 | 49.8523 | 0.99705
41 |  | 50 MVA 220/33 KV T/F-IInd at IIP Harrawala | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 40320 | 40298 | 385 | 39913 | 50 | 1 | 50 | 49.5223 | 0.99045
VII | 40 MVA
42 | E (O&M) 132 KV Kashipur | 40 MVA T/F-I (KSP-132) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 40320 | 40320 | 74 | 40246 | 40 | 1 | 40 | 39.9266 | 0.99816
43 |  | 40 MVA T/F-II (KSP-132) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 40320 | 40320 | 74 | 40246 | 40 | 1 | 40 | 39.9266 | 0.99816
44 |  | 40 MVA T/F-III (KSP-132) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 40320 | 40320 | 74 | 40246 | 40 | 1 | 40 | 39.9266 | 0.99816
45 |  | 40 MVA T/F (BZP S/S) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
46 |  | 40 MVA T/F (Ramnagar S/S) | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40310 | 0 | 40310 | 40 | 1 | 40 | 40 | 1
47 | E(O&M) 220 KV Mahuakherganj | 40 MVA T/F-I (Jaspur S/S) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 40320 | 40319 | 55 | 40264 | 40 | 1 | 40 | 39.9454 | 0.99864
48 |  | 40 MVA T/F-II (Jaspur S/S) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40319 | 0 | 40319 | 40 | 1 | 40 | 40 | 1
49 | E (O&M) 220 KV HALDWANI | 40 MVA-I 132/33 KV (HLD-220) | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40300 | 0 | 40300 | 40 | 1 | 40 | 40 | 1
50 |  | 40 MVA-II 132/33 KV (HLD-220) | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40300 | 0 | 40300 | 40 | 1 | 40 | 40 | 1
51 |  | 40 MVA-I 132/33 KV (HLD-132) | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40300 | 0 | 40300 | 40 | 1 | 40 | 40 | 1
52 |  | 40 MVA T/F 132/66 KV (HLD-132) | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 458 | 40320 | 40300 | 458 | 39842 | 40 | 1 | 40 | 39.5454 | 0.98864
53 | E (O&M) 220 KV Pantnagar | 40 MVA T/F Ist 132/33 KV at Kichha | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 40320 | 40320 | 290 | 40030 | 40 | 1 | 40 | 39.7123 | 0.99281
54 |  | 40 MVA T/F IInd 132/33 KV at Kichha | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 40320 | 40320 | 164 | 40156 | 40 | 1 | 40 | 39.8373 | 0.99593
55 |  | 40 MVA T/F I 132/33 KV at Rudrapur | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
56 |  | 40 MVA T/F II 132/33 KV at Rudrapur | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
57 | E (O&M) 220 KV Sitarganj | 40 MVA T/F-1 at Sitarganj S/S | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
58 |  | 40 MVA T/F-2 at Sitarganj S/S | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
59 |  | 40MVA T/F SITARGANJ SIDCUL1 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40284 | 0 | 40284 | 40 | 1 | 40 | 40 | 1
60 |  | 40MVA T/F SITARGANJ SIDCUL2 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40284 | 0 | 40284 | 40 | 1 | 40 | 40 | 1
61 | E (O&M) 220 KV Rishikesh | 40 MVA T/F-I (RKSH-220) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
62 |  | 40 MVA T/F-II (RKSH-220) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
63 | E (O&M) 220 KV Srinagar | 40 MVA 132/33kV T/F (132 SNR) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
64 | E (O&M) Dehradun | 40 MVA 132/33 KV T/F-Ist at Majra | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 40320 | 40320 | 404 | 39916 | 40 | 1 | 40 | 39.5992 | 0.98998
65 |  | 40 MVA 132/33 KV T/F-IInd at Majra | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40320 | 40320 | 22 | 40298 | 40 | 1 | 40 | 39.9782 | 0.99945
66 |  | 40 MVA 132/33 KV T/F-IIIrd at Majra | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40320 | 40320 | 22 | 40298 | 40 | 1 | 40 | 39.9782 | 0.99945
67 |  | 40 MVA T/F-I at Lalthapper S/S | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 40320 | 40320 | 135 | 40185 | 40 | 1 | 40 | 39.8661 | 0.99665
68 | E (O&M) Jhajhra | 40 MVA T/F-I at Jhajhra S/S | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
69 |  | 40 MVA 132/33 KV T/F-Ist at Bindal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
70 |  | 40 MVA 132/33 KV T/F-IInd at Bindal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
71 |  | 40 MVA T/F-I at Purkul S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40300 | 0 | 40300 | 40 | 1 | 40 | 40 | 1
72 | E (O&M) SIDCUL HRD | 40 MVA T/F-Ist (Jwalapur) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 40320 | 40320 | 303 | 40017 | 40 | 1 | 40 | 39.6994 | 0.99249
73 |  | 40 MVA T/F-II (Jwalapur) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 40320 | 40320 | 29 | 40291 | 40 | 1 | 40 | 39.9712 | 0.99928
74 |  | 40 MVA T/F-III (Jwalapur) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
75 | E (O&M) SIDCUL HRD | 40 MVA T/F-Ist (Bhoopatwala) | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40305 | 0 | 40305 | 40 | 1 | 40 | 40 | 1
76 |  | 40 MVA T/F-II (Bhoopatwala) | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40305 | 0 | 40305 | 40 | 1 | 40 | 40 | 1
77 |  | 40 MVA T/F-III (Bhoopatwala) | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 40320 | 40317 | 107 | 40210 | 40 | 1 | 40 | 39.8938 | 0.99735
78 |  | 40 MVA T/F-Ist (Kotdwar) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
79 |  | 40 MVA T/F-IInd (Kotdwar) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
80 | E (O&M) 220 KV Roorkee | 40 MVA T/F-Ist (Roorkee 132 ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
81 |  | 40 MVA T/F-III (Roorkee-132) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 40320 | 40320 | 42 | 40278 | 40 | 1 | 40 | 39.9583 | 0.99896
82 |  | 40 MVA T/F-Ist (Laksar 132 ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 40320 | 40320 | 20 | 40300 | 40 | 1 | 40 | 39.9802 | 0.9995
83 |  | 40 MVA T/F-II (Laksar 132) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
84 |  | 40 MVA T/F-Ist (Manglour) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 40 | 1 | 40 | 40 | 1
85 |  | 40 MVA T/F-IInd (Manglour) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 40320 | 40320 | 120 | 40200 | 40 | 1 | 40 | 39.881 | 0.99702
86 |  | 40 MVA T/F-Ist (Bhagwanpur) | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40311 | 0 | 40311 | 40 | 1 | 40 | 40 | 1
87 |  | 40 MVA T/F-IInd (Bhagwanpur) | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40311 | 0 | 40311 | 40 | 1 | 40 | 40 | 1
88 |  | 40 MVA T/F - (Bhagwanpur-132) | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 40320 | 40311 | 230 | 40081 | 40 | 1 | 40 | 39.7718 | 0.99429
89 |  | 40 MVA T/F - I Chudiyala | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40315 | 0 | 40315 | 40 | 1 | 40 | 40 | 1
90 |  | 40 MVA T/F- II Chudiyala | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40315 | 0 | 40315 | 40 | 1 | 40 | 40
VIII | 25 MVA
91 | E (O&M) 220 KV Srinagar | 25 MVA 220/33 KV T/F-Ist at chamba | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40320 | 40320 | 50 | 40270 | 25 | 1 | 25 | 24.969 | 0.99876
IX | 20 MVA
92 | E (O&M) 220 KV Srinagar | 20 MVA 132/33kV T/F (SNR S/S) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 20 | 1 | 20 | 20 | 1
93 |  | 20MVA T/F 132/66KV T/F (SNR S/S) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 20 | 1 | 20 | 20 | 1
94 |  | 20 MVA T/F-Ist (Satpuli-132) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 20 | 1 | 20 | 20 | 1
95 |  | 20 MVA T/F-II (Satpuli-132) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2085 | 40320 | 40320 | 2085 | 38235 | 20 | 1 | 20 | 18.9658 | 0.94829
96 |  | 20 MVA 132/33 KV T/F (132 SIMLI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 40320 | 40320 | 74 | 40246 | 20 | 1 | 20 | 19.9633
97 |  | 20 MVA 132/33kV T/F-II nd ( NGEF)Simli | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 40320 | 40320 | 74 | 40246 | 20 | 1 | 20 | 19.9633
98 | E (O&M) Jhajhra | 20 MVA 132/33 KV T/F-IInd at Purkul | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 20 | 1 | 20 | 20 | 1
99 | E (O&M) 220 KV Pantnagar | 20 MVA, 132/33 KV T/F at Rudrapur | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 20 | 1 | 20 | 20
100 | E (O&M) 132 KV Kashipur | 20 MVA T/F (Ramnagar S/S) | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40310 | 0 | 40310 | 20 | 1 | 20 | 20 | 1
101 | E (O&M) 220 KV Haldwani | 20 MVA T/F (Bhowali) | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40295 | 0 | 40295 | 20 | 1 | 20 | 20 | 1
102 | E (O&M) 220 KV Roorkee | 20 MVA T/F (Roorkee-220) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 20 | 1 | 20 | 20 | 1
103 |  | 20 MVA T/F - Ist (Roorkee-132) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 40320 | 40320 | 98 | 40222 | 20 | 1 | 20 | 19.9514 | 0.99757
104 |  | 20 MVA T/F - IInd (Roorkee-132) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 40320 | 40320 | 98 | 40222 | 20 | 1 | 20 | 19.9514 | 0.99757
105 | E (O&M) Almora | 20 MVA T/F -I (Pithoragarh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 40320 | 40320 | 20 | 40300 | 20 | 1 | 20 | 19.9901 | 0.9995
106 |  | 20 MVA T/F -II (Pithoragarh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 20 | 1 | 20 | 20 | 1
107 |  | 20 MVA T/F-Ist (Almora) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 40320 | 40320 | 28 | 40292 | 20 | 1 | 20 | 19.9861 | 0.99931
108 |  | 20 MVA T/F-IInd (Almora) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 40320 | 40320 | 28 | 40292 | 20 | 1 | 20 | 19.9861 | 0.99931
109 |  | 20 MVA T/F-IIIrd (Almora) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 40320 | 40320 | 28 | 40292 | 20 | 1 | 20 | 19.9861 | 0.99931
110 |  | 20 MVA T/F-IIIrd (Ranikhet) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 40320 | 40320 | 28 | 40292 | 20 | 1 | 20 | 19.9861 | 0.99931
X | 15 MVA
111 | E (O&M) Srinagar | 3X5 MVA 132/66kVT/F IInd (SNR S/S) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 15 | 1 | 15 | 15 | 1
112 | E (O&M) Haldwani | 3X5 MVA T/F-I 132/33 KV (Bhowali) | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40295 | 0 | 40295 | 15 | 1 | 15 | 15 | 1
113 |  | 3X5 MVA T/F-II 132/33 KV (Bhowali) | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40295 | 0 | 40295 | 15 | 1 | 15 | 15 | 1
114 | E (O&M) Almora | 3X5 MVA T/F-I (Pithoragarh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 40320 | 40320 | 14 | 40306 | 15 | 1 | 15 | 14.9948 | 0.99965
115 |  | 3X5 MVA T/F-IInd (Pithoragarh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 15 | 1 | 15 | 15 | 1
116 |  | 3X5 MVA T/F-Ist (Ranikhet) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 40320 | 40320 | 28 | 40292 | 15 | 1 | 15 | 14.9896 | 0.99931
117 |  | 3X5 MVA T/F-IInd (Ranikhet) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 40320 | 40320 | 28 | 40292 | 15 | 1 | 15 | 14.9896 | 0.99931
XI | 12.5 MVA
118 | E (O&M) 220 KV Rishikesh | 12.5 MVA T/F (RKSH-132) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40320 | 40320 | 0 | 40320 | 12.5 | 1 | 12.5 | 12.5 | 1
|  | (ii): Total for ICTs | [5 empty] | 7487.5 | 7442.2566 | 0.99396
N = Total No. of ICTs (I+II+III+IV+…+X)
* SLDC has to verify the outage period for reasonableness of time for restoration of the element as per Clause 6(a) & 6(b) of Appendix 2 to the Regulations.